## Heaters
<Agency>
HVAC Systems Checklist
To be filled out by HVAC crew chief
File No.
Equipment Information Existing □ Replacement □
Make: |  |  | Model: | Serial:
Fuel Type: □ Natural □ Propane Forced Air: □ Yes □ No Btuh Input: ____________________________
Furnace Type: □ Draft hood □ 80% □ 90% □ Mobile home Age of unit_____________ NM Gas □ Yes □ No
Application: □ Up flow □ Down flow □ Horizontal □ Lowboy □ Package |  |  |  | □ Other: | □ PERMIT
Furnace Location (CAZ):
Water Heater Location (CAZ) |  |  |  | □ Gas | □ Electric | Btuh Input:
Reading | Initials | FUEL LEAKS
All fuel leaks repaired and retested
Flexible gas lines replaced if:
Line kinked, corroded, worn or entering air handler cabinet
Line connection is soldered or two-piece type
Line manufactured before 1973 per dated metal ring on line
Line runs directly to gas valve
ALL HEATING EQUIPMENT
Limit Switch shuts off burner at 200⁰ F.
Gas pressure within appropriate range for appliance
Venting proper
Combustion air enough for appliance
NEW INSTALLATIONS
CO Testing Under Worse Case
Draft under worse case within range (Use outside temperature and formula)
Static Pressure return and supply within label range
Temperature Rise within range
Blower speed set appropriately for equipment and ducts
All penetrations sealed
Condensation line follows SWS
Voltage, voltage drop, and grounding follows SWS, manufacturer, and local codes
Room to room balancing, less than 3pascals
Client education SWS (CO, maintenance, basic operation, air blocking, thermostat)
EXISTING EQUIPMENT
Cracked or broken blower belts replaced
Motor amperage measured and appropriate size pulley installed on belt drive
Clean furnace filter installed and extra left with client
Blower or Air Handler visually or physically inspected, cleaned, oiled
Other necessary cleaning. Indicate air intakes, burners, furnace controls, heat
exchangers, blower compartment, return air plenum, registers, grilles
Thermostat replaced if needed and/or client is provided proper education on thermostat
Other tests conducted if needed
Deration needed, proper fuel type
Condition of heat exchanger
Combustion Safety Test Action Levels
Carbon Monoxide Result |  | And/Or | Spillage and Draft Test | Action
0 – 25 ppm |  | And | Passes | Proceed with work
26 – 100 ppm |  | And | Passes | Recommend that the CO problem be
fixed
26 – 100 ppm |  | And | Fails at worst case only | Recommend a service call for the
appliance and/or repairs to the home
to correct the problem
100 – 400 ppm |  | Or | Fails under natural conditions | Stop Work: Work may not proceed
until the system is serviced and the
problem is corrected
> 400 ppm |  | And | Passes | Stop Work: Work may not proceed
until the system is serviced and the
problem is corrected
> 400 ppm |  | And | Fails under any condition | Emergency: Shut off fuel to the
appliance and have the homeowner to
call for service immediately
CAZ Limits (for reference)
Venting Conditions | [6 empty] | Limit (Pa)
Orphan natural draft water heater (including outside chimneys) | [6 empty] | -2
Natural draft boiler or furnace commonly vented with water heater | [6 empty] | -3
Natural draft boiler or furnace with damper commonly vented with water heater | [6 empty] | -5
Induced draft boiler or furnace commonly vented with water heater | [6 empty] | -5
Individual natural draft boiler or furnace | [6 empty] | -5
Closed , controlled wood-burning appliances | [6 empty] | -7
Power vented or induced draft boiler or furnace alone, or fan assisted DWH alone | [6 empty] | -15
Pellet stove with exhaust fan and sealed vent | [6 empty] | -15
Direct vented appliances; Sealed combustion appliances forced draft; Chimney-top draft inducer | [6 empty] | -25

## Water heaters
<Agency>
Water heater Checklist
To be filled out by HVAC crew chief
File No.
Equipment Information Existing □ Replacement □
Make: |  |  | Model: | Serial:
Fuel Type: □ Natural □ Propane Btuh Input: ____________________________ □ Electric KW input________
Water heater type : □ Sealed combustion □ Mobile home Other □ Age of unit_____________ NM Gas □ Yes □ No
Location: □ Outside closet □ CAZ inside □ Other:____________________________ | [5 empty] | □ PERMIT
Furnace Location (CAZ):
Water Heater Location (CAZ) |  |  |  | □ Gas | □ Electric | Btuh Input:
Reading | Initials | FUEL LEAKS
All fuel leaks repaired and retested
Flexible gas lines replaced if:
Line kinked, corroded, worn or entering air handler cabinet
Line connection is soldered or two-piece type
Line manufactured before 1973 per dated metal ring on line
Line runs directly to gas valve
ALL WATER HEATING EQUIPMENT
Hazardous materials removed, client education carried out
Water leaks repaired
Relief valve compliant with 2012 IRC, local code, and SWS
Venting proper
Combustion air enough for appliance
Discharge temperature at 120 degrees with proper client education carried out
Client education SWS (CO, maintenance, basic operation, air blocking, temperature)
Wiring up to all applicable codes if electric
NEW INSTALLATIONS
CO Testing Under Worse Case
Draft under worse case within range (Use outside temperature and formula)
Equipment selected is either direct vent, or power vented
Equipment selected is Energy Star
Equipmetn selected meets other SWS requirements
All penetrations sealed
Drain pan follows local codes and SWS
Expansion tank SWS compliant
Di-electric unions installed and meets all local code and SWS requirements
Backflow prevention meets SWS and code requirements
Insulation at R-11 or higher on tank, lines insulated to SWS
Installation meets other SWS and code requirements
EXISTING EQUIPMENT
Corrosion noted or replacement reccomended based on general condition
Combustion safety testing verified with energy auditor, retest if needed
Location of unit is code and SWS compliant
Derated properly for altitude and fuel type
Mobile home unit for mobile home
Combustion Safety Test Action Levels
Carbon Monoxide Result |  | And/Or | Spillage and Draft Test | Action
0 – 25 ppm |  | And | Passes | Proceed with work
26 – 100 ppm |  | And | Passes | Recommend that the CO problem be
fixed
26 – 100 ppm |  | And | Fails at worst case only | Recommend a service call for the
appliance and/or repairs to the home
to correct the problem
100 – 400 ppm |  | Or | Fails under natural conditions | Stop Work: Work may not proceed
until the system is serviced and the
problem is corrected
> 400 ppm |  | And | Passes | Stop Work: Work may not proceed
until the system is serviced and the
problem is corrected
> 400 ppm |  | And | Fails under any condition | Emergency: Shut off fuel to the
appliance and have the homeowner to
call for service immediately
CAZ Limits (for reference)
Venting Conditions | [6 empty] | Limit (Pa)
Orphan natural draft water heater (including outside chimneys) | [6 empty] | -2
Natural draft boiler or furnace commonly vented with water heater | [6 empty] | -3
Natural draft boiler or furnace with damper commonly vented with water heater | [6 empty] | -5
Induced draft boiler or furnace commonly vented with water heater | [6 empty] | -5
Individual natural draft boiler or furnace | [6 empty] | -5
Closed , controlled wood-burning appliances | [6 empty] | -7
Power vented or induced draft boiler or furnace alone, or fan assisted DWH alone | [6 empty] | -15
Pellet stove with exhaust fan and sealed vent | [6 empty] | -15
Direct vented appliances; Sealed combustion appliances forced draft; Chimney-top draft inducer | [6 empty] | -25

## Sheet3
<Agency>
HVAC Systems - Replacement Unit
Cient Name: |  | File No. |  | Date:
HVAC Installer:
Equipment Information
Fuel Type: □ Natural □ Propane Forced Air: □ Yes □ No Btuh Input:
Furnace Type: □ Draft hood □ 80% □ 90% □ Mobile home |  |  | □ Other:
Application: □ Up flow □ Down flow □ Horizontal □ Lowboy □ Package
Make: | Model: |  | Serial:
Furnace Location (CAZ): |  |  | Water Heater: | □ Gas | □ Electric
WH Location (CAZ) |  |  | Btuh Input:
Installation complies with all SWS and local codes? □ Comment if contrary to SWS________________
______________________________________________________________________________________________
______________________________________________________________________________________________
Revised 1/17/2012